## ADM4, 6
ADAM-4000/6000 Model |  |  |  | Analog Input | [8 empty] | Analog Output |  |  |  |  | Digital Input |  |  |  | Digital Output |  |  | Relay Output | [5 empty] | General | [8 empty] | Environmental |  |  | Protocol & Web Related | [5 empty] | Gateway (General Spec) | [5 empty] | Certification | [5 empty] | EOL | Note
ADM4/ ADM6 | Type | Model | Description | Resolution | Sampling Rate | Channels | Thermocouple or RTD Type | Current Input | Voltage Input | Accuracy | Burn-out Detection | Input Impedance | Resolution | Channels | Voltage Output | Current Output | Accuracy | Channels | Dry Contact | Wet Contact | Others | Channels | Sink /Source | Type | Channels | Breakdown Voltage | Contact Rating (Resistive) | Relay On Time (Typical) | Relay Off Time (Typical) | Max. Operating Speed | Connectors | LAN | Power Input | Power Reversal Protection | Power Consumption | Isolation | Watchdog Timer | Over Voltage Protection | Built-in TVS/ESD Protection | Operation Temperature | Storage Temperature | Operating Humidity | ASCII Command | Modbus /RTU | Modbus/TCP | Azure IoT Hub | Web Language Support | RESTful | MCU | Memory | Storage | OS | Programming | Communication | CE | FCC | UL | C1D2 | KCC | Others
ADM4 | AI/O | ADAM-4015-CE | 6-ch RTD Module with Modbus | 16-bit | 10 sample/ second (total) | 6 x RTD | Pt 100, Pt 1000, Balco 500, Ni 508 | - | - | Voltage mode: ±0.1% or better Current mode: ±0.2% or better | Yes (4 ~ 20 mA) | 10 MΩ | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 x plug-in terminal blocks (#14 ~ 28 AWG) | - | 10 ~ 30 VDC | Y | 1.2 W @ 24 VDC | 3,000 VDC | System & Com. | - | - | -10 ~ 70°C (14 ~ 158°F) | -25 ~ 85°C (-13 ~ 185°F) | 5 ~ 95% RH | Y | Y | - | - | - | - | - | - | - | - | - | - | Y | - | Y | Y | Y | - | No EOL Plan
ADM4 | AI/O | ADAM-4017+-CE | 8-ch Analog Input Module with Modbus | 16-bit | 10 sample/ second (total) | 8 x AI | V, A | 4 ~ 20 mA, ±20 mA | ±150 mV, ±500 mV, ±1 V, ±5 V, ±10 V | Voltage mode: ±0.1% or better Current mode: ±0.2% or better | - | Voltage: 20 MΩ Current: 120 Ω | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 x plug-in terminal blocks (#14 ~ 22 AWG) | - | 10 ~ 30 VDC | Y | 1.2 W @ 24 VDC | 3,000 VDC | System & Com. | ±35 VDC | Y | -10 ~ 70°C (14 ~ 158°F) | -25 ~ 85°C (-13 ~ 185°F) | 5 ~ 95% RH | Y | Y | - | - | - | - | - | - | - | - | - | - | Y | Y | Y | Y | Y | - | No EOL Plan
ADM4 | AI/O | ADAM-4017-D2E | 8-ch Analog Input Module | 16-bit | 10 sample/ second (total) | 8 x AI | V, A | ±20 mA | ±150 mV, ±500 mV, ±1 V, ±5 V, ±10 V | ±0.1% or better | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 x plug-in terminal blocks (#14 ~ 22 AWG) | - | 10 ~ 30 VDC | Y | 1.2 W @ 24 VDC | 3,000 VDC | System | - | - | -10 ~ 70°C (14 ~ 158°F) | -25 ~ 85°C (-13 ~ 185°F) | 5 ~ 95% RH | Y | - | - | - | - | - | - | - | - | - | - | - | Y | Y | Y | - | Y | - | No EOL Plan
ADM4 | AI/O | ADAM-4018+-BE | 8-ch Thermocouple Input Module with Modbus | 16-bit | 10 sample/ second (total) | 8 x AI/TC | mA, Thermocouple: J, K, T, E, R, S, B | 4 ~ 20 mA, ±20 mA | - | Voltage mode: ±0.1% or better Current mode: ±0.2% or better | Yes (4 ~ 20 mA & All T/C) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 x plug-in terminal blocks (#14 ~ 22 AWG) | - | 10 ~ 30 VDC | Y | 0.8 W @ 24 VDC | 3,000 VDC | System & Com. | ±35 VDC | Y | -10 ~ 70°C (14 ~ 158°F) | -25 ~ 85°C (-13 ~ 185°F) | 5 ~ 95% RH | Y | Y | - | - | - | - | - | - | - | - | - | - | Y | Y | Y | Y | Y | - | No EOL Plan
ADM4 | AI/O | ADAM-4019+-AE | 8-ch Universal Analog Input Module with Modbus | 16-bit | 10 sample/ second (total) | 8 x AI/TC | mV, V, mA, Thermocouple: J, K, T, E, R, S, B | 4 ~ 20 mA, ±20 mA | ±100 mV, ±500 mV,±1 V, ±2.5 V, ±5 V, ±10 V, | Voltage mode: ±0.1% or better Current mode: ±0.2% or better | Yes (4 ~ 20 mA & All T/C) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 x plug-in terminal blocks (#14 ~ 22 AWG) | - | 10 ~ 30 VDC | Y | 1 W @ 24 VDC | 3,000 VDC | System & Com. | ±35 VDC | Y | -10 ~ 70°C (14 ~ 158°F) | -25 ~ 85°C (-13 ~ 185°F) | 5 ~ 95% RH | Y | Y | - | - | - | - | - | - | - | - | - | - | Y | Y | Y | Y | Y | - | No EOL Plan
ADM4 | AI/O | ADAM-4021-DE | 1-ch Analog Output Module | - | - | - | - | - | - | - | - | - | 12-bit | 1 | 0 ~ 10 V | 0 ~ 20 mA, 4 ~ 20 mA | Voltage mode: ±0.2% or better Current mode: ±0.1% or better | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 x plug-in terminal | - | 10 ~ 30 VDC | Y | 1.4 W @ 24 VDC | 3,000 VDC | System | - | - | -10 ~ 70°C (14 ~ 158°F) | -25 ~ 85°C (-13 ~ 185°F) | 5 ~ 95% RH | Y | - | - | - | - | - | - | - | - | - | - | - | Y | - | Y | - | Y | - | No EOL Plan
ADM4 | AI/O | ADAM-4024-B1E | 4-ch Analog Output Module with Modbus | - | - | - | - | - | - | - | - | - | 12-bit | 4 | ±10 V | 0 ~ 20 mA, 4 ~ 20 mA | Voltage mode: ±0.1% or better Current mode: ±0.1% or better | 4 | - | Logic 0: 1 V max. Logic 1: 10~ 30 V | See column "Note" | - | - | - | - | - | - | - | - | - | 2 x plug-in terminal blocks (#14 ~ 28 AWG) | - | 10 ~ 30 VDC | Y | 3 W @ 24 VDC | 3,000 VDC | System & Com. | - | - | -10 ~ 70°C (14 ~ 158°F) | -25 ~ 85°C (-13 ~ 185°F) | 5 ~ 95% RH | Y | Y | - | - | - | - | - | - | - | - | - | - | Y | Y | Y | Y | Y | - | No EOL Plan | Non-isolation input level (programmable threshold): - Logic level 0: 0 to 0.8V (default = 0.8 V) - Logic level 1: 2.4 to 5V (default = 2.4 V) - Gate Logic level 0: 0.8 V max - Gate Logic level 1: 2.4 to 5V
ADM4 | DI/O | ADAM-4050-DE | 15-ch Digital I/O Module | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 7 | - | Logic 0:1 V max. Logic 1:3.5 ~ 30 V | - | 8 | Sink | open collector to 30 V, 30 mA maximum load | - | - | - | - | - | - | 2 x plug-in terminal blocks (#14 ~ 22 AWG) | - | 10 ~ 30 VDC | Y | 0.4 W @ 24 VDC | - | System | - | - | -10 ~ 70°C (14 ~ 158°F) | -25 ~ 85°C (-13 ~ 185°F) | 5 ~ 95% RH | Y | - | - | - | - | - | - | - | - | - | - | - | Y | Y | Y | - | Y | - | No EOL Plan
ADM4 | DI/O | ADAM-4051-BE | 16-ch Isolated Digital Input Module with Modbus | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 16 | Logic 0: Open Logic 1: Close to ground | Logic 0:3 V max. Logic 1:10 ~ 50 V | - | - | - | - | - | - | - | - | - | - | 2 x plug-in terminal blocks (#14 ~ 28 AWG) | - | 10 ~ 30 VDC | Y | 1 W @ 24 VDC | 2,500 VDC | System | - | - | -10 ~ 70°C (14 ~ 158°F) | -25 ~ 85°C (-13 ~ 185°F) | 5 ~ 95% RH | Y | Y | - | - | - | - | - | - | - | - | - | - | Y | Y | Y | Y | Y | - | No EOL Plan
ADM4 | DI/O | ADAM-4052-BE | 8-ch Isolated Digital Input Module | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 8 | - | Logic 0:1 V max Logic 1:3 ~ 30 V | - | - | - | - | - | - | - | - | - | - | 2 x plug-in terminal blocks (#14 ~ 22 AWG) | - | 10 ~ 30 VDC | Y | 0.4 W @ 24 VDC | 5,000 VRMS | System | - | - | -10 ~ 70°C (14 ~ 158°F) | -25 ~ 85°C (-13 ~ 185°F) | 5 ~ 95% RH | Y | - | - | - | - | - | - | - | - | - | - | - | Y | Y | Y | - | Y | - | No EOL Plan
ADM4 | DI/O | ADAM-4053-AE | 16-ch Digital Input Module | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 16 | Logic 0: Close to ground Logic 1: Open | Logic 0:2 V max Logic 1:4 ~ 30 V | - | - | - | - | - | - | - | - | - | - | 2 x plug-in terminal blocks (#14 ~ 22 AWG) | - | 10 ~ 30 VDC | Y | 1 W @ 24 VDC | - | System | - | - | -10 ~ 70°C (14 ~ 158°F) | -25 ~ 85°C (-13 ~ 185°F) | 5 ~ 95% RH | Y | - | - | - | - | - | - | - | - | - | - | - | Y | Y | Y | - | Y | - | No EOL Plan
ADM4 | DI/O | ADAM-4055-BE | 16-ch Isolated Digital I/O Module with Modbus | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 8 | Logic 0: Open Logic 1: Close to ground | Logic 0:3 V max. Logic 1:10 ~ 50 V | - | 8 | Sink | open collector to 40 V, 200 mA maximum load | - | - | - | - | - | - | 2 x plug-in terminal blocks (#14 ~ 28 AWG) | - | 10 ~ 30 VDC | Y | 1 W @ 24 VDC | 2,500 VDC | System & Com. | - | - | -10 ~ 70°C (14 ~ 158°F) | -25 ~ 85°C (-13 ~ 185°F) | 5 ~ 95% RH | Y | Y | - | - | - | - | - | - | - | - | - | - | Y | Y | Y | - | Y | - | No EOL Plan
ADM4 | DI/O | ADAM-4056S-AE | 12-ch Sink Type Isolated Digital Output Module with Modbus | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12 | Sink | open collector to 40 V, 200 mA maximum load | - | - | - | - | - | - | 2 x plug-in terminal blocks (#14 ~ 22 AWG) | - | 10 ~ 30 VDC | Y | 1.5 W @ 24 VDC | 5,000 VDC | System & Com. | - | - | -10 ~ 70°C (14 ~ 158°F) | -25 ~ 85°C (-13 ~ 185°F) | 5 ~ 95% RH | Y | Y | - | - | - | - | - | - | - | - | - | - | Y | Y | Y | - | Y | - | No EOL Plan
ADM4 | DI/O | ADAM-4056SO-AE | 12-ch Source Type Isolated Digital Output Module with Modbus | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12 | Source | Voltage Range: 10 ~ 35 VDC  Current: 1 A (per channel) | - | - | - | - | - | - | 2 x plug-in terminal blocks (#14 ~ 22 AWG) | - | 10 ~ 30 VDC | Y | 1.5 W @ 24 VDC | 5,000 VDC | System & Com. | - | - | -10 ~ 70°C (14 ~ 158°F) | -25 ~ 85°C (-13 ~ 185°F) | 5 ~ 95% RH | Y | Y | - | - | - | - | - | - | - | - | - | - | Y | Y | Y | Y | Y | - | No EOL Plan
ADM4 | Relay Output | ADAM-4060-DE | 4-ch Relay Output Module | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 Form A, 2 Form C | 500 VAC (50/60 Hz) | 0.6 A @ 125 VAC 0.3 A @ 250 VAC 2 A @ 30 VDC 0.6 A @ 110 VDC | 3 ms | 2 ms | 20 operations/min (at rated load) | 2 x plug-in terminal blocks (#14 ~ 22 AWG) | - | 10 ~ 30 VDC | Y | 0.8 W @ 24 VDC | - | System | - | - | -10 ~ 70°C (14 ~ 158°F) | -25 ~ 85°C (-13 ~ 185°F) | 5 ~ 95% RH | Y | - | - | - | - | - | - | - | - | - | - | - | Y | Y | - | - | Y | - | No EOL Plan
ADM4 | Relay Output | ADAM-4068-BE | 8-ch Relay Output Module with Modbus | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 4 Form A, 4 Form C | 500 VAC (50/60 Hz) | 0.5 A @ 120 VAC 0.25 A @ 240 VAC 1 A @ 30 VDC 0.3 A @ 110 VDC | 3 ms | 4 ms | 50 operations/min (at rated load) | 2 x plug-in terminal blocks (#14 ~ 28 AWG) | - | 10 ~ 30 VDC | Y | 0.6 W @ 24 VDC | - | System & Com. | - | - | -10 ~ 70°C (14 ~ 158°F) | -25 ~ 85°C (-13 ~ 185°F) | 5 ~ 95% RH | Y | Y | - | - | - | - | - | - | - | - | - | - | Y | Y | - | - | Y | - | No EOL Plan
ADM4 | Relay Output | ADAM-4069-AE | 8-ch Power Relay Output Module with Modbus | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 4 Form A, 4 Form C | 1,000 VAC (50/60 Hz) | 5 A @ 250 VAC 5 A @ 30 VDC | 5 ms | 5.6 ms | 6 operations/min (at rated load) | 2 x plug-in terminal blocks (#14 ~ 28 AWG) | - | 10 ~ 30 VDC | Y | 2.2 W @ 24 VDC | - | System & Com. | - | - | -10 ~ 70°C (14 ~ 158°F) | -25 ~ 85°C (-13 ~ 185°F) | 5 ~ 95% RH | Y | Y | - | - | - | - | - | - | - | - | - | - | Y | Y | Y | - | - | - | No EOL Plan
ADM4 | DI/O | ADAM-4080-E | 2-ch Counter/Frequency Modules | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 Independent counters | - | Logic 0: 1 V max. Logic 1: 3.5~ 30 V | - | 2 | Sink | open collector to 30 V, 30 mA maximum load | - | - | - | - | - | - | 2 x plug-in terminal blocks (#14 ~ 22 AWG) | - | 10 ~ 30 VDC | Y | 2 W @ 24 VDC | 2,500 VDC | System | - | - | -10 ~ 70°C (14 ~ 158°F) | -25 ~ 85°C (-13 ~ 185°F) | 5 ~ 95% RH | Y | Y | - | - | - | - | - | - | - | - | - | - | Y | Y | Y | - | Y | - | No EOL Plan
ADM4 | AI/O | ADAM-4115-B | Robust 6-Ch RTD Input Module | 16-bit | 10 or 100 samples/second (total) | 6 x RTD | Pt 100, Pt 1000, Balco 500, Ni 50, Ni 508 | - | - | Voltage mode: ±0.1% or better Current mode: ±0.2% or better | Yes (4 ~ 20 mA) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 x plug-in terminal blocks (#14 ~ 22 AWG) | - | 10 ~ 48 VDC | Y | 1.2 W @ 24 VDC | 3,000 VDC | System | - | - | -40 ~ 85°C (-40 ~ 185°F) | -40 ~ 85°C (-40 ~ 185°F) | 5 ~ 95% RH | Y | Y | - | - | - | - | - | - | - | - | - | - | Y | - | Y | - | - | - | No EOL Plan
ADM4 | AI/O | ADAM-4117-B | Robust 8-ch Analog Input Module with Modbus | 16-bit | 10 or 100 samples/second (total) | 8 x AI | V, A | 0 ~ 20mA , 4 ~ 20mA , ±20mA | 0 ~ 150mV, 0 ~ 500mV, 0 ~ 1V, 0 ~ 5V, 0 ~ 10V, 0 ~ 15V, ±150 mV, ±500 mV, ±1V, ±5 V, ±10 V, ±15V | Voltage mode: ±0.1% or better Current mode: ±0.2% or better | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 x plug-in terminal blocks (#14 ~ 22 AWG) | - | 10 ~ 48 VDC | Y | 1.2 W @ 24 VDC | 3,000 VDC | System & Com. | ±60 VDC | Y | -40 ~ 85°C (-40 ~ 185°F) | -40 ~ 85°C (-40 ~ 185°F) | 5 ~ 95% RH | Y | Y | - | - | - | - | - | - | - | - | - | - | Y | Y | Y | Y | - | - | No EOL Plan
ADM4 | AI/O | ADAM-4118-B | Robust 8-ch Thermocouple Input Module with Modbus | 16-bit | 10 or 100 samples/second (total) | 8 x AI/TC | V, A, Thermocouple: J, K, T, E, R, S, B | 4 ~ 20 mA, 0 ~ 20 mA | ±15 mV, ±50 mV, ±100 mV, ±500 mV, ±1 V, ±2.5 V | Voltage mode: ±0.1% or better Current mode: ±0.2% or better | Yes (4 ~ 20 mA) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 x plug-in terminal blocks (#14 ~ 22 AWG) | - | 10 ~ 48 VDC | Y | 0.5W @ 24 VDC | 3,000 VDC | System & Com. | ±60 VDC | Y | -40 ~ 85°C (-40 ~ 185°F) | -40 ~ 85°C (-40 ~ 185°F) | 5 ~ 95% RH | Y | Y | - | - | - | - | - | - | - | - | - | - | Y | Y | Y | Y | - | - | No EOL Plan
ADM4 | DI/O | ADAM-4150-B | Robust 15-ch Digital I/O Module with Modbus | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 7 | Logic 0: Close to ground Logic 1: Open | Logic 0: 3 VDC Logic 1: 10 ~ 30 VDC | - | 8 | Sink | open collector to 40 V, 800 mA maximum load | - | - | - | - | - | - | 2 x plug-in terminal blocks (#14 ~ 22 AWG) | - | 10 ~ 48 VDC | Y | 0.7 W @ 24 VDC | 3,000 VDC | System & Com. | - | - | -40 ~ 85°C (-40 ~ 185°F) | -40 ~ 85°C (-40 ~ 185°F) | 5 ~ 95% RH | Y | Y | - | - | - | - | - | - | - | - | - | - | Y | Y | Y | Y | - | - | No EOL Plan | (The Digital Input Level 0 and 1 status can be inverted)
ADM4 | Relay Output | ADAM-4168-B | Robust 8-ch Relay Output Module with Modbus | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 8 Form A | 750 VAC (50/60 Hz) | 0.5 A @ 120 VAC 0.25 A @ 240 VAC 1 A @ 30 VDC 0.3 A @ 110 VDC | 3 ms | 1 ms | 50 operations/min (at rated load) | 2 x plug-in terminal blocks (#14 ~ 22 AWG) | - | 10 ~ 48 VDC | Y | 1.8 W @ 24 VDC | 3,000 VDC | System & Com. | - | - | -40 ~ 85°C (-40 ~ 185°F) | -40 ~ 85°C (-40 ~ 185°F) | 5 ~ 95% RH | Y | Y | - | - | - | - | - | - | - | - | - | - | Y | Y | Y | - | - | - | No EOL Plan
ADM4 | Converter/Repeater | ADAM-4510-EE | RS-422/485 Repeater | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 x plug-in terminal blocks (#14 ~ 22 AWG) (RS-422/485) | - | 10 ~ 30 VDC | Y | 1.4 W @ 24 VDC | - | - | - | - | -10 ~ 70°C (14 ~ 158°F) | -25 ~ 85°C (-13 ~ 185°F) | 5 ~ 95% RH | Y | - | - | - | - | - | - | - | - | - | - | - | - | Y | Y | - | Y | - | No EOL Plan
ADM4 | Converter/Repeater | ADAM-4510I-AE | Robust RS-422/485 Repeater | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 x plug-in terminal blocks (#14 ~ 22 AWG) | - | 10 ~ 48 VDC | Y | 1.4 W @ 24 VDC | 3,000 VDC | - | - | - | -40 ~ 85°C (-40 ~ 185°F) | -40 ~ 85°C (-40 ~ 185°F) | 5 ~ 95% RH | Y | - | - | - | - | - | - | - | - | - | - | - | Y | Y | Y | Y Groups A,B,C,D Hazardous Location | - | - | No EOL Plan
ADM4 | Converter/Repeater | ADAM-4510S-EE | RS-422/485 Repeater | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 x plug-in terminal blocks (#14 ~ 22 AWG) (RS-422/485) | - | 10 ~ 30 VDC | Y | 1.4 W @ 24 VDC | 3,000 VDC | - | - | - | -10 ~ 70°C (14 ~ 158°F) | -25 ~ 85°C (-13 ~ 185°F) | 5 ~ 95% RH | Y | - | - | - | - | - | - | - | - | - | - | - | - | Y | Y | - | Y | - | No EOL Plan
ADM4 | Converter/Repeater | ADAM-4520-EE | Isolated RS-232 to RS-422/485 Converter | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 x plug-in terminal block (#14 ~ 22 AWG) (RS-422/485) 1 x DB9-F (RS-232) | - | 10 ~ 30 VDC | Y | 1.2 W @ 24 VDC | 3,000 VDC | - | - | - | -10 ~ 70°C (14 ~ 158°F) | -25 ~ 85°C (-13 ~ 185°F) | 5 ~ 95% RH | Y | - | - | - | - | - | - | - | - | - | - | - | Y | - | - | - | Y | - | No EOL Plan
ADM4 | Converter/Repeater | ADAM-4520I-AE | Robust RS-232 to RS-422/485 Converter | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 x plug-in terminal block (#14 ~ 22 AWG) (RS-422/485) 1 x DB9-F (RS-232) | - | 10 ~ 48 VDC | Y | 1.2 W @ 24 VDC | 3,000 VDC | - | - | - | -40 ~ 85°C (-40 ~ 185°F) | -40 ~ 85°C (-40 ~ 185°F) | 5 ~ 95% RH | Y | - | - | - | - | - | - | - | - | - | - | - | Y | Y | Y | Y Groups A,B,C,D Hazardous Location | - | - | No EOL Plan
ADM4 | Converter/Repeater | ADAM-4521-AE | Addressable RS-422/485 to RS-232 Converter | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 x plug-in terminal block (#14 ~ 22 AWG) (RS-422/485) 1 x DB9-F (RS-232) | - | 10 ~ 30 VDC | Y | 1 W @ 24 VDC | 1,000 VDC | Built-in microprocessor and watchdog timer | - | - | -10 ~ 70°C (14 ~ 158°F) | -25 ~ 85°C (-13 ~ 185°F) | 5 ~ 95% RH | Y | - | - | - | - | - | - | - | - | - | - | - | Y | - | Y | - | - | - | No EOL Plan
ADM4 | Converter/Repeater | ADAM-4541-BE | Multi-mode Fiber Optic to RS-232/422/485 Converter | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 x plug-in terminal block (#14 ~ 22 AWG) (RS-232/422/485) 2 x ST fiber connector | - | 10 ~ 30 VDC | Y | 1.5 W @ 24 VDC | - | - | - | - | -10 ~ 70°C (14 ~ 158°F) | -25 ~ 85°C (-13 ~ 185°F) | 5 ~ 95% RH | Y | - | - | - | - | - | - | - | - | - | - | - | Y | - | Y | - | Y | FM | No EOL Plan
ADM4 | Converter/Repeater | ADAM-4542+-BE | Single-mode Fiber Optic to RS-232/422/485 Converter | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 x plug-in terminal block (#14 ~ 22 AWG) (RS-232/422/485) 2 x SC fiber connector | - | 10 ~ 30 VDC | Y | 3 W @ 24 VDC | - | - | - | - | -10 ~ 70°C (14 ~ 158°F) | -25 ~ 85°C (-13 ~ 185°F) | 5 ~ 95% RH | Y | - | - | - | - | - | - | - | - | - | - | - | Y | Y | Y | - | - | - | No EOL Plan
ADM4 | Converter/Repeater | ADAM-4561-CE | 1-port Isolated USB to RS-232/422/485 Converter | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | Serial: 1 x plug-in terminal (#14 ~ 22 AWG) (3-wire RS-232/422/485) Network: USB-type A connector (type A to type B cable provided) | - | Powered by USB port | - | 1.5 W @ 5 VDC | 3,000 VDC | - | - | - | -10 ~ 70°C (14 ~ 158°F) | -25 ~ 85°C (-13 ~ 185°F) | 5 ~ 95% RH | Y | - | - | - | - | - | - | - | - | - | - | - | Y | Y | Y | - | Y | - | No EOL Plan
ADM4 | Converter/Repeater | ADAM-4562-AE | 1-port Isolated USB to RS-232/422/485 Converter | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | Serial:1 x DB-9 serial connectors (9-wire RS-232) Network: USB-type A connector (type A to type B cable provided) | - | Powered by USB port | - | 1.1 W @ 5 VDC | 2,500 VDC | - | - | - | -10 ~ 70°C (14 ~ 158°F) | -25 ~ 85°C (-13 ~ 185°F) | 5 ~ 95% RH | Y | - | - | - | - | - | - | - | - | - | - | - | Y | Y | Y | - | - | - | No EOL Plan
ADM6 | AI/O | ADAM-6015-DE | 7-ch Isolated RTD Input Modbus TCP Module | 16-bit | 10 sample/ second (total) | 7 x RTD | Pt 100, Pt 1000, Balco 500, Ni 508 | - | - | ±0.1 % or better High speed mode:±0.5% or better | Yes (4 ~ 20 mA) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 x RJ-45 (LAN), Plug-in screw terminal block (I/O and power) | - | 10 ~ 30 VDC | Y | 2.5 W @ 24 VDC | 2,000 VDC | System & Com. | - | Y | -10 ~ 70°C (14 ~ 158°F); -40 ~ 70°C (-40~158°F) for D version | -20 ~ 80°C (-4 ~ 176°F); -40 ~ 85°C ( -40~185°F) for D version | 20 ~ 95% RH (non-condensing | Y | - | Y | - | - | Y | - | - | - | - | - | - | Y | Y | Y | Y | Y | - | No EOL Plan
ADM6 | AI/O | ADAM-6017-D | 8-ch Isolated Analog Input Modbus TCP Module with 2-ch DO | 16-bit | 10 or 100 samples/second (total) | 8 x AI | V, A | 0 ~ 20mA , 4 ~ 20mA , ±20mA | 0 ~ 150mV, 0 ~ 500mV, 0 ~ 1V, 0 ~ 5V, 0 ~ 10V, ±150mV, ±500mV , ±1V, ±5V, ±10V | Voltage mode: ±0.1% or better Current mode: ±0.2% or better | Yes (4 ~ 20 mA) | - | - | - | - | - | - | - | - | - | - | 2 | Sink | open collector to 30 V | - | - | - | - | - | - | 1 x RJ-45 (LAN), Plug-in screw terminal block (I/O and power) | 10/100Base-T(X) | 10 ~ 30 VDC | Y | 2.7 W @ 24 VDC | 2,000 VDC | System & Com. | - | - | -10 ~ 70°C (14 ~ 158°F); -40 ~ 70°C (-40~158°F) for D version | -20 ~ 80°C (-4 ~ 176°F); -40 ~ 85°C ( -40~185°F) for D version | 20 ~ 95% RH (non-condensing | Y | - | Y | Y | - | Y | - | - | - | - | - | - | Y | Y | Y | Y | Y | - | No EOL Plan
ADM6 | AI/O | ADAM-6018+-D | 8-ch Isolated Thermocouple Input Module | 16-bit | 10 sample/ second (total) | 8 x TC | V, A, Thermocouple: J, K, T, E, R, S, B | - | - | @25°C Type J,K,E,R,S: ±0.1% FSR Max Type B: ±0.15% FSR Max Type T: ±0.2% FSR Max | Yes (4 ~ 20 mA) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 x RJ-45 (LAN), Plug-in screw terminal block (I/O and power) | - | 10 ~ 30 VDC | Y | 1 W @ 24 VDC | 2,000 VDC | System & Com. | - | - | -10 ~ 70°C (14 ~ 158°F); -40 ~ 70°C (-40~158°F) for D version | -20 ~ 80°C (-4 ~ 176°F); -40 ~ 85°C ( -40~185°F) for D version | 20 ~ 95% RH (non-condensing | Y | - | Y | - | - | Y | - | - | - | - | - | - | Y | Y | Y | Y | - | - | No EOL Plan
ADM6 | AI/O | ADAM-6022-A1E | Ethernet-based Dual-loop PID Controller | 16-bit | 10 sample/ second (total) | 6 x AI | V, A | 4 ~ 20 mA, 0 ~ 20 mA | ±10 VDC | Voltage mode: ±0.1% or better Current mode: ±0.2% or better | - | - | 12-bit | 2 | 0 ~ 10 V | 0 ~ 20 mA, 4 ~ 20 mA | ±0.1% of FSR | 2 | Logic 0: Close to ground Logic 1: Open | Logic 0: 0 ~ 3 VDC Logic 1: 10 ~ 30 VDC | - | 2 | Sink | open collector to 30 V | - | - | - | - | - | - | 1 x RJ-45 (LAN), Plug-in screw terminal block (I/O and power) | 10/100Base-T(X) | 10 ~ 30 VDC | Y | 4 W @ 24 VDC | 2,000 VDC | System & Com. | - | Y | -10 ~ 50°C(14 ~ 122° F); -40 ~ 70°C (-40~158°F) for D version | -20 ~ 80° C(-4 ~ 176° F); -40 ~ 85°C ( -40~185°F) for D version | 20 ~ 95% RH (non-condensing | Y | - | Y | - | - | Y | - | - | - | - | - | - | Y | Y | Y | Y | - | - | No EOL Plan | Loop Number: 2 (3 AI, 1 AO, 1 DI, 1 DO for each control loop)
ADM6 | AI/O | ADAM-6024-A1E | 12-ch Isolated Universal Input/Output Modbus TCP Module | 16-bit | 10 sample/ second (total) | 6 x AI | V, A | 4 ~ 20 mA, 0 ~ 20 mA | ±10 VDC | Voltage mode: ±0.1% or better Current mode: ±0.2% or better | Yes (4 ~ 20 mA) | - | 12-bit | 2 | 0 ~ 10 V | 0 ~ 20 mA, 4 ~ 20 mA | ±0.1% of FSR | 2 | Logic 0: Close to ground Logic 1: Open | Logic 0: 0 ~ 3 VDC Logic 1: 10 ~ 30 VDC | - | 2 | Sink | open collector to 40 V | - | - | - | - | - | - | 1 x RJ-45 (LAN), Plug-in screw terminal block (I/O and power) | 10/100Base-T(X) | 10 ~ 30 VDC | Y | 4 W @ 24 VDC | 2,000 VDC | System & Com. | - | Y | -10 ~ 50°C(14 ~ 122° F); -40 ~ 70°C (-40~158°F) for D version | -20 ~ 80° C(-4 ~ 176° F); -40 ~ 85°C ( -40~185°F) for D version | 20 ~ 95% RH (non-condensing | Y | - | Y | - | - | Y | - | - | - | - | - | - | Y | Y | Y | Y | Y | - | EOL in Jun 2020
ADM6 | AI/O | ADAM-6024-D | 12-ch Isolated Universal Input/Output Modbus TCP Module | 16-bit | 10 sample/ second (total) | 6 x AI | V, A | 4 ~ 20 mA, 0 ~ 20 mA | ±10 VDC | Voltage mode: ±0.1% or better Current mode: ±0.2% or better | Yes (4 ~ 20 mA) | - | 12-bit | 2 | 0 ~ 10 V | 0 ~ 20 mA, 4 ~ 20 mA | ±0.1% of FSR | 2 | Logic 0: Close to ground Logic 1: Open | Logic 0: 0 ~ 3 VDC Logic 1: 10 ~ 30 VDC | - | 2 | Sink | open collector to 40 V | - | - | - | - | - | - | 1 x RJ-45 (LAN), Plug-in screw terminal block (I/O and power) | 10/100Base-T(X) | 10 ~ 30 VDC | Y | 4 W @ 24 VDC | 2,000 VDC | System & Com. | - | Y | -10 ~ 50°C(14 ~ 122° F); -40 ~ 70°C (-40~158°F) for D version | -20 ~ 80° C(-4 ~ 176° F); -40 ~ 85°C ( -40~185°F) for D version | 20 ~ 95% RH (non-condensing | Y | - | Y | - | - | Y | - | - | - | - | - | - | Y | Y | Y | Y | Y | - | No EOL Plan
ADM6 | DI/O | ADAM-6050-D | 18-ch Isolated Digital I/O Modbus TCP Module | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12 | Logic 0: Close to ground Logic 1: Open | Logic 0: 0 ~ 3 VDC Logic 1: 10 ~ 30 VDC | - | 6 | Sink | open collector to 30 V, 100 mA maximum load | - | - | - | - | - | - | 1 x RJ-45 (LAN), Plug-in screw terminal block (I/O and power) | 10/100Base-T(X) | 10 ~ 30 VDC | Y | 2 W @ 24 VDC | 2,000 VDC | System & Com. | - | - | -20 ~ 70°C (14 ~ 158°F); -40 ~ 70°C (-40~158°F) for D version | -30 ~ 80°C(-22 ~ 176°F); -40 ~ 80°C (-40~176°F) for D version | 20 ~ 95% RH (non-condensing | Y | - | Y | Y | - | Y | - | - | - | - | - | - | Y | Y | - | Y | Y | - | No EOL Plan |  Supports 3 kHz Counter Input(32-bit + 1-bit overflow)  Keep/Discard Counter Value when Power-off  Supports 3 kHz Frequency Input  Supports Inverted DI Status
ADM6 | DI/O | ADAM-6051-D | 14-ch Isolated Digital I/O Modbus TCP Module with 2-ch Counter | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12 | Logic 0: Close to ground Logic 1: Open | Logic 0: 0 ~ 3 VDC Logic 1: 10 ~ 30 VDC | - | 2 | Sink | open collector to 30 V, 100 mA maximum load | - | - | - | - | - | - | 1 x RJ-45 (LAN), Plug-in screw terminal block (I/O and power) | 10/100Base-T(X) | 10 ~ 30 VDC | Y | 2 W @ 24 VDC | 2,000 VDC | System & Com. | - | - | -20 ~ 70°C (14 ~ 158°F); -40 ~ 70°C (-40~158°F) for D version | -30 ~ 80°C(-22 ~ 176°F); -40 ~ 80°C (-40~176°F) for D version | 20 ~ 95% RH (non-condensing | Y | - | Y | Y | - | Y | - | - | - | - | - | - | Y | Y | - | Y | Y | - | No EOL Plan |  Supports 3 kHz Counter Input(32-bit + 1-bit overflow)  Keep/Discard Counter Value when Power-off  Supports 3 kHz Frequency Input  Supports Inverted DI Status
ADM6 | DI/O | ADAM-6052-D | 16-ch Source-type Isolated Digital I/O Modbus TCP Module | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 8 | Logic 0: Close to ground Logic 1: Open | Logic 0: 0 ~ 3 VDC Logic 1: 10 ~ 30 VDC | - | 8 | Source | Voltage Range: 10 ~ 35 VDC  Current: 1 A (per channel) | - | - | - | - | - | - | 1 x RJ-45 (LAN), Plug-in screw terminal block (I/O and power) | 10/100Base-T(X) | 10 ~ 30 VDC | Y | 2 W @ 24 VDC | 2,000 VDC | System & Com. | - | - | -20 ~ 70°C (14 ~ 158°F); -40 ~ 70°C (-40~158°F) for D version | -30 ~ 80°C(-22 ~ 176°F); -40 ~ 80°C (-40~176°F) for D version | 20 ~ 95% RH (non-condensing | Y | - | Y | Y | - | Y | - | - | - | - | - | - | Y | Y | - | Y | Y | - | No EOL Plan |  Supports 3 kHz Counter Input(32-bit + 1-bit overflow)  Keep/Discard Counter Value when Power-off  Supports 3 kHz Frequency Input  Supports Inverted DI Status
ADM6 | Relay Output | ADAM-6060-D | 6-ch Digital Input and 6-ch Relay Modbus TCP Module | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 6 | Logic 0: Close to ground Logic 1: Open | Logic 0: 3 VDC Logic 1: 10 ~ 30 VDC | - | - | - | - | 6 Form A | 500 VAC (50/60 Hz) | 0.5 A @ 120 VAC 1 A @ 30 VDC | 7 ms | 3 ms | 20 operations/min (at rated load) | 1 x RJ-45 (LAN), Plug-in screw terminal block (I/O and power) | 10/100Base-T(X) | 10 ~ 30 VDC | Y | 2 W @ 24 VDC | 2,000 VDC | System & Com. | - | - | -10 ~ 70°C (14 ~ 158°F); -40 ~ 70°C (-40~158°F) for D version | -20 ~ 80°C (-4 ~ 176°F); -40 ~ 80°C (-40~176°F) for D version | 20 ~ 95% RH (non-condensing | Y | - | Y | Y | - | - | - | - | - | - | - | - | Y | Y | Y | - | Y | - | No EOL Plan |  Supports 3 kHz Counter Input (32-bit + 1-bit overflow)  Keep/Discard Counter Value when Power-off  Supports 3 kHz Frequency Input  Supports Inverted DI Status
ADM6 | Relay Output | ADAM-6066-D | 6-ch Digital Input and 6-ch Power Relay Modbus TCP Module | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 6 | Logic 0: Close to ground Logic 1: Open | Logic 0: 3 VDC Logic 1: 10 ~ 30 VDC | - | - | - | - | 6 Form A | 500 VAC (50/60 Hz) | 5 A @ 250 VAC 3 A @ 30 VDC | 7 ms | 3 ms | 20 operations/min (at rated load) | 1 x RJ-45 (LAN), Plug-in screw terminal block (I/O and power) | 10/100Base-T(X) | 10 ~ 30 VDC | Y | 2.5 W @ 24 VDC | 2,000 VDC | System & Com. | - | - | -10 ~ 70°C (14 ~ 158°F); -40 ~ 70°C (-40~158°F) for D version | -20 ~ 80°C (-4 ~ 176°F); -40 ~ 80°C (-40~176°F) for D version | 20 ~ 95% RH (non-condensing | Y | - | Y | Y | - | - | - | - | - | - | - | - | Y | Y | Y | - | - | - | No EOL Plan |  Supports 3 kHz Counter Input (32-bit + 1-bit overflow)  Keep/Discard Counter Value when Power-off  Supports 3 kHz Frequency Input  Supports Inverted DI Status
ADM6 | AI/O | ADAM-6117EI-AE | 8-ch Isolated Analog Input EtherNet/IP Module | 16-bit | 10 sample/ second (total) | 8 x AI | V, A | 0 ~ 20mA , 4 ~ 20mA , ±20mA | ±150 mV, ±500 mV, ±1 V, ±5 V, ±10 V | Voltage mode: ±0.1% or better Current mode: ±0.2% or better | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2x RJ-45 LAN, Plug-in screw terminal block (I/O and power) | 10/100Base-T(X) | 10 ~ 30 VDC | Y | 3.5 W @ 24 VDC | 2,500 VDC | System | - | Y | -10 ~ 70°C (14 ~ 158°F) | -20 ~ 80°C (-4 ~ 176°F) | 20 ~ 95% RH (non-condensing | Y | - | - | - | - | - | - | - | - | - | - | - | Y | Y | - | - | - | - | No EOL Plan
ADM6 | AI/O | ADAM-6117PN-AE | 8-ch Isolated AI PROFINET Module | 16-bit | 10 sample/ second (total) | 8 x AI | V, A | 0 ~ 20mA , 4 ~ 20mA , ±20mA | ±150 mV, ±500 mV, ±1 V, ±5 V, ±10 V | Voltage mode: ±0.1% or better Current mode: ±0.2% or better | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2x RJ-45 LAN, Plug-in screw terminal block (I/O and power) | 10/100Base-T(X) | 10 ~ 30 VDC | Y | 3.5 W @ 24 VDC | 2,500 VDC | System | - | Y | -10 ~ 70°C (14 ~ 158°F) | -20 ~ 80°C (-4 ~ 176°F) | 20 ~ 95% RH (non-condensing | Y | - | - | - | - | - | - | - | - | - | - | - | Y | Y | - | - | - | - | No EOL Plan
ADM6 | DI/O | ADAM-6150EI-AE | 15-ch Isolated Digital I/O EtherNet/IP Module | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 8 | Logic 0: Open Logic 1: Closed to DGND | Logic 0: 0 ~ 3 VDC or 0 ~ -3 VDC Logic 1: 10 ~ 30 VDC or -10 ~ -30 VDC | - | 7 | Sink | Voltage Range: 8 ~ 35 VDC Normal Output Current: 100 mA (per channel) | - | - | - | - | - | - | 2x RJ-45 LAN, Plug-in screw terminal block (I/O and power) | 10/100Base-T(X) | 10 ~ 30 VDC | Y | 3 W @ 24 VDC | 2,500 VDC | System | - | - | -10 ~ 70°C (14 ~ 158°F) | -20 ~ 80°C (-4 ~ 176°F) | 20 ~ 95% RH (non-condensing | Y | - | - | - | - | - | - | - | - | - | - | - | Y | Y | - | - | - | - | No EOL Plan | Dry/Wet Contact decided by switch
ADM6 | DI/O | ADAM-6150PN-AE | 15-ch Isolated Digital I/O PROFINET Module | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 8 | Logic 0: Open Logic 1: Closed to DGND | Logic 0: 0 ~ 3 VDC or 0 ~ -3 VDC Logic 1: 10 ~ 30 VDC or -10 ~ -30 VDC | - | 7 | Sink | Voltage Range: 8 ~ 35 VDC Normal Output Current: 100 mA (per channel) | - | - | - | - | - | - | 2x RJ-45 LAN, Plug-in screw terminal block (I/O and power) | 10/100Base-T(X) | 10 ~ 30 VDC | Y | 3 W @ 24 VDC | 2,500 VDC | System | - | - | -10 ~ 70°C (14 ~ 158°F) | -20 ~ 80°C (-4 ~ 176°F) | 20 ~ 95% RH (non-condensing | Y | - | - | - | - | - | - | - | - | - | - | - | Y | Y | - | - | - | - | No EOL Plan | Dry/Wet Contact decided by switch
ADM6 | DI/O | ADAM-6151EI-AE | 16-ch Isolated Digital Input EtherNet/IP Module | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 16 | Logic 0: Open Logic 1: Closed to DGND | Logic 0: 0 ~ 3 VDC or 0 ~ -3 VDC Logic 1: 10 ~ 30 VDC or -10 ~ -30 VDC | - | - | - | - | - | - | - | - | - | - | 2x RJ-45 LAN, Plug-in screw terminal block (I/O and power) | 10/100Base-T(X) | 10 ~ 30 VDC | Y | 2.7 W @ 24 VDC | 2,500 VDC | System | - | - | -10 ~ 70°C (14 ~ 158°F) | -20 ~ 80°C (-4 ~ 176°F) | 20 ~ 95% RH (non-condensing | Y | - | - | - | - | - | - | - | - | - | - | - | Y | Y | - | - | - | - | No EOL Plan
ADM6 | DI/O | ADAM-6151PN-AE | 16-ch Isolated Digital Input PROFINET Module | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 16 | Logic 0: Open Logic 1: Closed to DGND | Logic 0: 0 ~ 3 VDC or 0 ~ -3 VDC Logic 1: 10 ~ 30 VDC or -10 ~ -30 VDC | - | - | - | - | - | - | - | - | - | - | 2x RJ-45 LAN, Plug-in screw terminal block (I/O and power) | 10/100Base-T(X) | 10 ~ 30 VDC | Y | 2.7 W @ 24 VDC | 2,500 VDC | System | - | - | -10 ~ 70°C (14 ~ 158°F) | -20 ~ 80°C (-4 ~ 176°F) | 20 ~ 95% RH (non-condensing | Y | - | - | - | - | - | - | - | - | - | - | - | Y | Y | - | - | - | - | No EOL Plan
ADM6 | DI/O | ADAM-6156EI-AE | 16-ch Isolated Digital Output EtherNet/IP Module | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 16 | Sink | Voltage Range: 8 ~ 35 VDC Normal Output Current: 100 mA (per channel) | - | - | - | - | - | - | 2x RJ-45 LAN, Plug-in screw terminal block (I/O and power) | 10/100Base-T(X) | 10 ~ 30 VDC | Y | 3.2 W @ 24 VDC | 2,500 VDC | System | - | - | -10 ~ 70°C (14 ~ 158°F) | -20 ~ 80°C (-4 ~ 176°F) | 20 ~ 95% RH (non-condensing | Y | - | - | - | - | - | - | - | - | - | - | - | Y | Y | - | - | - | - | No EOL Plan
ADM6 | DI/O | ADAM-6156PN-AE | 16-ch Isolated Digital Output PROFINET Module | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 16 | Sink | Voltage Range: 8 ~ 35 VDC Normal Output Current: 100 mA (per channel) | - | - | - | - | - | - | 2x RJ-45 LAN, Plug-in screw terminal block (I/O and power) | 10/100Base-T(X) | 10 ~ 30 VDC | Y | 3.2 W @ 24 VDC | 2,500 VDC | System | - | - | -10 ~ 70°C (14 ~ 158°F) | -20 ~ 80°C (-4 ~ 176°F) | 20 ~ 95% RH (non-condensing | Y | - | - | - | - | - | - | - | - | - | - | - | Y | Y | - | - | - | - | No EOL Plan
ADM6 | Relay Output | ADAM-6160EI-AE | 6-ch Relay Output EtherNet/IP Module | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 5 Form C, 1 Form A | 500 VAC (50/60 Hz) | 5 A @ 250 VAC 5 A @ 30 VDC | 8 ms | 8 ms | 360 operations/hour with load | 2x RJ-45 LAN, Plug-in screw terminal block (I/O and power) | 10/100Base-T(X) | 10 ~ 30 VDC | Y | 4.5 W @ 24 VDC | 2,500 VDC | System | - | - | -10 ~ 70°C (14 ~ 158°F) | -20 ~ 80°C (-4 ~ 176°F) | 20 ~ 95% RH (non-condensing | Y | - | - | - | - | - | - | - | - | - | - | - | Y | Y | - | - | - | - | No EOL Plan
ADM6 | Relay Output | ADAM-6160PN-AE | 6-ch Relay PROFINET Module | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 5 Form C, 1 Form A | 500 VAC (50/60 Hz) | 5 A @ 250 VAC 5 A @ 30 VDC | 8 ms | 8 ms | 360 operations/hour with load | 2x RJ-45 LAN, Plug-in screw terminal block (I/O and power) | 10/100Base-T(X) | 10 ~ 30 VDC | Y | 4.5 W @ 24 VDC | 2,500 VDC | System | - | - | -10 ~ 70°C (14 ~ 158°F) | -20 ~ 80°C (-4 ~ 176°F) | 20 ~ 95% RH (non-condensing | Y | - | - | - | - | - | - | - | - | - | - | - | Y | Y | - | - | - | - | No EOL Plan
ADM6 | AI/O | ADAM-6217-B | 8-ch Isolated Analog Input Modbus TCP Module | 16-bit | 10 sample/ second (total) | 8 x AI | V, A | 0 ~ 20mA , 4 ~ 20mA , ±20mA | ±150 mV, ±500 mV, ±1 V, ±5 V, ±10 V | Voltage mode: ±0.1% or better Current mode: ±0.2% or better | - | Voltage: 10 MΩ Current: 120 Ω | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2x RJ-45 LAN Plug-in 5P/15P screw terminal blocks | 10/100Base-T(X) | 10 ~ 30 VDC | Y | 3.5 W @ 24 VDC | 2,500 VDC | System & Com. | - | - | -10 ~ 70°C (14 ~ 158°F); -40 ~ 70°C (-40~158°F) for B version | -20 ~ 80°C (-4 ~ 176°F); -40 ~ 80°C ( -40~176°F) for B version | 20 ~ 95% RH (non-condensing | Y | - | Y | Y | XML, HTML 5, Java Script | - | - | - | - | - | - | - | Y | Y | - | - | Y | - | No EOL Plan
ADM6 | AI/O | ADAM-6224-B | 4-ch Isolated Analog Output Modbus TCP Module | - | - | - | - | - | - | - | - | - | 12-bit | 4 | 0 ~ 5 V, 0 ~ 10 V, ± 5 V, ± 10 V | 0 ~ 20 mA, 4 ~ 20 mA | ±0.3% of FSR (Voltage) ±0.5% of FSR (Current) | 4 | Logic 0: Open Logic 1: Closed to DGND | - | - | - | - | - | - | - | - | - | - | - | 2x RJ-45 LAN Plug-in 5P/15P screw terminal blocks | 10/100Base-T(X) | 10 ~ 30 VDC | Y | 6W @ 24 VDC | 2,500 VDC | System & Com. | - | - | -10 ~ 70°C (14 ~ 158°F); -40 ~ 70°C (-40~158°F) for B version | -20 ~ 80°C (-4 ~ 176°F); -40 ~ 80°C ( -40~176°F) for B version | 20 ~ 95% RH (non-condensing | Y | - | Y | - | XML, HTML 5, Java Script | - | - | - | - | - | - | - | Y | Y | - | - | - | - | No EOL Plan |  Support DI Filter  Support Inverted DI Status  Support Trigger to Startup or Safety Value
ADM6 | DI/O | ADAM-6250-B | 15-ch Isolated Digital I/O Modbus TCP Module | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 8 | Logic 0: Open Logic 1: Closed to DGND | Logic 0: 0 ~ 3 VDC or 0 ~ -3 VDC Logic 1: 10 ~ 30 VDC or -10 ~ -30 VDC | - | 7 | Sink | Voltage Range: 10 ~ 30 VDC Normal Output Current: 100 mA (per channel) | - | - | - | - | - | - | 2x RJ-45 LAN Plug-in 5P/15P screw terminal blocks | 10/100Base-T(X) | 10 ~ 30 VDC | Y | 3 W @ 24 VDC | 2,500 VDC | System & Com. | - | - | -10 ~ 70°C (14 ~ 158°F); -40 ~ 70°C (-40~158°F) for B version | -20 ~ 80°C (-4 ~ 176°F); -40 ~ 80°C ( -40~176°F) for B version | 20 ~ 95% RH (non-condensing | Y | - | Y | Y | XML, HTML 5, Java Script | - | - | - | - | - | - | - | Y | Y | - | - | Y | - | No EOL Plan |  ◎DI: Frequency Input Range 0.1 ~ 3kHz  Counter Input 3kHz (32 bit + 1 bit overflow)  Keep/Discard Counter Value when power off  Supports Inverted DI Status Dry/Wet Contact decided by switch  ◎DO:  Pulse Output Up to 5kHz  Delay Output High-to-Low and Low-to-High
ADM6 | DI/O | ADAM-6251-B | 16-ch Isolated Digital Input Modbus TCP Module | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 16 | Logic 0: Open Logic 1: Closed to DGND | Logic 0: 0 ~ 3 VDC or 0 ~ -3 VDC Logic 1: 10 ~ 30 VDC or -10 ~ -30 VDC | - | - | - | - | - | - | - | - | - | - | 2x RJ-45 LAN Plug-in 5P/15P screw terminal blocks | 10/100Base-T(X) | 10 ~ 30 VDC | Y | 2.7 W @ 24 VDC | 2,500 VDC | System & Com. | - | - | -10 ~ 70°C (14 ~ 158°F); -40 ~ 70°C (-40~158°F) for B version | -20 ~ 80°C (-4 ~ 176°F); -40 ~ 80°C ( -40~176°F) for B version | 20 ~ 95% RH (non-condensing | Y | - | Y | Y | XML, HTML 5, Java Script | - | - | - | - | - | - | - | Y | Y | - | - | - | - | No EOL Plan |  Frequency Input Range 0.1 ~ 3kHz  Counter Input 3kHz (32 bit + 1 bit overflow)  Keep/Discard Counter Value when power off  Supports Inverted DI Status
ADM6 | DI/O | ADAM-6256-B | 16-ch Isolated Digital Output Modbus TCP Module | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 16 | Sink | Voltage Range: 10 ~ 30 VDC Normal Output Current: 100 mA (per channel) | - | - | - | - | - | - | 2x RJ-45 LAN Plug-in 5P/15P screw terminal blocks | 10/100Base-T(X) | 10 ~ 30 VDC | Y | 3.2 W @ 24 VDC | 2,500 VDC | System & Com. | - | - | -10 ~ 70°C (14 ~ 158°F); -40 ~ 70°C (-40~158°F) for B version | -20 ~ 80°C (-4 ~ 176°F); -40 ~ 80°C ( -40~176°F) for B version | 20 ~ 95% RH (non-condensing | Y | - | Y | Y | XML, HTML 5, Java Script | - | - | - | - | - | - | - | Y | Y | - | - | Y | - | No EOL Plan |  Pulse Output Up to 5kHz  Delay Output High-to-Low and Low-to-High
ADM6 | Relay Output | ADAM-6260-B | 6-ch Relay Output Modbus TCP Module | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 5 Form C, 1 Form A | 500 VAC (50/60 Hz) | 5 A @ 250 VAC 5 A @ 30 VDC | 8 ms | 8 ms | 360 operations/hour with load | 2x RJ-45 LAN Plug-in 5P/15P screw terminal blocks | 10/100Base-T(X) | 10 ~ 30 VDC | Y | 4.5 W @ 24 VDC | 2,500 VDC | System & Com. | - | - | -10 ~ 70°C (14 ~ 158°F); -40 ~ 70°C (-40~158°F) for B version | -20 ~ 80°C (-4 ~ 176°F); -40 ~ 80°C ( -40~176°F) for B version | 20 ~ 95% RH (non-condensing | Y | - | Y | Y | XML, HTML 5, Java Script | - | - | - | - | - | - | - | Y | Y | - | - | - | - | No EOL Plan
ADM6 | Relay Output | ADAM-6266-B | 4-ch Relay Output Modbus TCP Module with 4-ch DI | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 4 | Logic 0: Open Logic 1: Closed to DI COM | Logic 0: 0 ~ 3 VDC or 0 ~ -3 VDC Logic 1: 10 ~ 30 VDC or -10 ~ -30 VDC | - | - | - | - | 4 Form C | 500 VAC (50/60 Hz) | 5 A @ 250 VAC 5 A @ 30 VDC | 8 ms | 8 ms | 360 operations/hour with load | 2x RJ-45 LAN Plug-in 5P/15P screw terminal blocks | 10/100Base-T(X) | 10 ~ 30 VDC | Y | 4.2 W @ 24 VDC | 2,500 VDC | System & Com. | - | - | -10 ~ 70°C (14 ~ 158°F); -40 ~ 70°C (-40~158°F) for B version | -20 ~ 80°C (-4 ~ 176°F); -40 ~ 80°C ( -40~176°F) for B version | 20 ~ 95% RH (non-condensing | Y | - | Y | Y | XML, HTML 5, Java Script | - | - | - | - | - | - | - | Y | Y | - | - | Y | - | No EOL Plan
ADM6 | I/O Gateway | ADAM-6717-A | Intelligent I/O Gateway with Analog Input | 16-bit | 10 or 100 samples/second (total) | 8 x AI | V, A | 0 ~ 20mA , 4 ~ 20mA , ±20mA | 0 ~ 150mV, 0 ~ 500mV, 0 ~ 1V, 0 ~ 5V, 0 ~ 10V, ±150mV, ±500mV , ±1V, ±5V, ±10V | Voltage mode: ±0.1% or better Current mode: ±0.2% or better | - | - | - | - | - | - | - | 5 | Logic 0: Open Logic 1: Close to ground | Logic 0: 0 ~ 3 VDC Logic 1: 10 ~ 30 VDC | - | 4 | Sink | open collector to 30 V, 100 mA maximum load | - | - | - | - | - | - | 2x RJ-45 LAN, Plug-in screw terminal block (I/O and power) | 10/100Base-T(X) | 10 ~ 30 VDC | Y | 6W @ 24 VDC | 2,500 VDC | System & Com. | - | - | -40 ~ 70 °C (-40~158 °F) | -40 ~ 85°C (-40 ~ 185°F) | 40 °C @85% RH (non-condensing) | Y | Y | Y | - | - | - | Cortex-A8 32-Bit 1GHz | DDR3L 512MB | NAND flash 512MB for system storage; microSD Slot (Optional) | RT Linux V3.12 | Node-RED, Linux C |  LAN port 2 x RJ-45 10/100 Mbps(2MAC ID)  Serial port: 2 x RS-485  USB port: 1 x Type-A USB, 1 x Micro USB (Client) | Y | Y | - | - | - | - | No EOL Plan
ADM6 | I/O Gateway | ADAM-6750-A | Intelligent I/O Gateway with Digital I/O | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12 | Logic 0: Open Logic 1: Close to ground | Logic 0: 0 ~ 3 VDC Logic 1: 10 ~ 30 VDC | - | 12 | Sink | open collector to 30 V, 100 mA maximum load | - | - | - | - | - | - | 2x RJ-45 LAN, Plug-in screw terminal block (I/O and power) | 10/100Base-T(X) | 10 ~ 30 VDC | Y | 6W @ 24 VDC | 2,500 VDC | System & Com. | - | - | -40 ~ 70 °C (-40~158 °F) | -40 ~ 85°C (-40 ~ 185°F) | 40 °C @85% RH (non-condensing) | Y | Y | Y | - | - | - | Cortex-A8 32-Bit 1GHz | DDR3L 512MB | NAND flash 512MB for system storage; microSD Slot (Optional) | RT Linux V3.12 | Node-RED, Linux C |  LAN port 2 x RJ-45 10/100 Mbps(2MAC ID)  Serial port: 2 x RS-485  USB port: 1 x Type-A USB, 1 x Micro USB (Client) | Y | Y | - | - | - | - | No EOL Plan | ◎DI: Support 3KHz counter input ◎DO: Support 3KHz pulse output